## Sever 基本資料
Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue
機櫃/Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack
廠牌/Vendor | Supermicro | Supermicro | HPE | Dell Inc. | N/A | Supermicro | N/A | Supermicro | N/A | N/A | Intel Corporation | Dell Inc. | Dell Inc.
Model | AS-1115HS-TNR | SYS-111E-WR | ProLiant DL380 Gen10 | PowerEdge R750 | N/A | SSG-6028R-E1CR12L | N/A | SYS-521E-WR | N/A | N/A | S2600WFT | PowerEdge R750 | PowerEdge R740
序號/Serial Number | A515042X5816356 | A497720X4813116 | SGH146Y31S | CNIVC0029B0942 | N/A | A17487427611634 | N/A | A497706X4200296 | N/A | N/A | WO152116L01S001 | CNFCP0032L00VK | CNIVC0022P2057
U Position | U18-U18 | U22-U22 | U28-U29 | U31-U32 | U37-U38 | U8-U9 | U12-U13 | U15-U16 | U23-U24 | U31-U32 | U33-U34 | U35-U36 | U37-U38
IP | 192.168.10.81 | 192.168.10.87 | 192.168.10.125 | 192.168.8.222 | 192.168.10.128 | 192.168.10.88 | 192.168.10.74 | 192.168.10.92 | 192.168.10.121 | 192.168.10.94 | 192.168.10.75 | 192.168.10.123 | 192.168.10.124
Online Status | Online | Online | Online | Online | Offline | Online | Offline | Online | Offline | Offline | Online | Online | Online
Redfish Configured | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Redfish Data Available | Yes | Yes | Yes | Yes | No/Offline | Yes | No | Yes | No | No | Yes | Yes | Yes
Redfish power(server-level) | Yes | Yes | Yes | Yes | N/A | Yes | N/A | Yes | N/A | N/A | N/A | Yes | Yes
Node Exporter Configured | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | N/A | N/A | Yes | Yes | Yes
Node Exporter Data Available | Partial | Partial | Partial | Partial | No | Yes | No | Partial | NO | No | NO | Yes | Not checked
PDU Name | PDU [Raritan] PX4-5256CR-C8E8A0 | No outlet mapping shown | No outlet mapping shown | PDU [Raritan] PX4-5256CR-C8E8A0 | No outlet mapping shown | PDU [Raritan] PX4-5256CR-C8E8A0 | No | PDU [Raritan] PX4-5256CR-C8E8A0 | No | PDU [Raritan] PX4-5256CR-C8E8A0 | PDU [Raritan] PX4-5256CR-C8E8A0 | PDU [Raritan] PX4-5256CR-C8E8A0 | PDU [Raritan] PX4-5256CR-C8E8A0
PDU Relationship | Yes | No | No | Yes | No | Yes(Power relationship in topology) | No | Yes | No | Yes | Yes | Yes | Yes
PDU Outlet | Outlet 5 | Unknown | Unknown | Outlet 12 | Unknown | Outlet 9 | Unknown | Outlet 11 | Unknown | Outlet 4 | Outlet 8 | Outlet 6 | Outlet 10
Health Status Available | Yes | Yes | Yes | Yes | no | Yes | no | Yes | Yes | Yes | Yes | Yes | Yes
Research Usability | High | Medium | Medium | High | Low | High | Low | High | Low | Low | Medium | High | High
Server | 機櫃/Rack | 廠牌/Vendor | Model | 序號/Serial Number | U Position | IP | Online Status | Redfish Configured | Redfish Data Available | Redfish power(server-level) | Node Exporter Configured | Node Exporter Data Available | PDU Name | PDU Relationship | PDU Outlet | Health Status Available | Research Usability
Quine | BMW New-Rack | Supermicro | AS-1115HS-TNR | A515042X5816356 | U18-U18 | 192.168.10.81 | Online | Yes | Yes | Yes | Yes | Partial | PDU [Raritan] PX4-5256CR-C8E8A0 | Yes | Outlet 5 | Yes | High
Maxwell | BMW New-Rack | Supermicro | SYS-111E-WR | A497720X4813116 | U22-U22 | 192.168.10.87 | Online | Yes | Yes | Yes | Yes | Partial | No outlet mapping shown | No | Unknown | Yes | Medium
Davinci | BMW New-Rack | HPE | ProLiant DL380 Gen10 | SGH146Y31S | U28-U29 | 192.168.10.125 | Online | Yes | Yes | Yes | Yes | Partial | No outlet mapping shown | No | Unknown | Yes | Medium
Joule | BMW New-Rack | Dell Inc. | PowerEdge R750 | CNIVC0029B0942 | U31-U32 | 192.168.8.222 | Online | Yes | Yes | Yes | Yes | Partial | PDU [Raritan] PX4-5256CR-C8E8A0 | Yes | Outlet 12 | Yes | High
Einstein | BMW New-Rack | N/A | N/A | N/A | U37-U38 | 192.168.10.128 | Offline | Yes | No | N/A | Yes | No | No outlet mapping shown | No | Unknown | no | Low
Newton | BMW Old-Rack | Supermicro | SSG-6028R-E1CR12L | A17487427611634 | U8-U9 | 192.168.10.88 | Online | Yes | Yes | Yes | Yes | Yes | PDU [Raritan] PX4-5256CR-C8E8A0 | Yes(Power relationship in topology) | Outlet 9 | Yes | High
Bell | BMW Old-Rack | N/A | N/A | N/A | U12-U13 | 192.168.10.74 | Offline | Yes | No | N/A | Yes | No | No | No | Unknown | no | Low
Lavoisier | BMW Old-Rack | Supermicro | SYS-521E-WR | A497706X4200296 | U15-U16 | 192.168.10.92 | Online | Yes | Yes | Yes | Yes | Partial | PDU [Raritan] PX4-5256CR-C8E8A0 | Yes | Outlet 11 | Yes | High
Ohm | BMW Old-Rack | N/A | N/A | N/A | U23-U24 | 192.168.10.121 | Offline | Yes | No | N/A | N/A | NO | No | No | Unknown | Yes | Low
Galileo | BMW Old-Rack | N/A | N/A | N/A | U31-U32 | 192.168.10.94 | Offline | Yes | No | N/A | N/A | No | PDU [Raritan] PX4-5256CR-C8E8A0 | Yes | Outlet 4 | Yes | Low
Archmedies | BMW Old-Rack | Intel Corporation | S2600WFT | WO152116L01S001 | U33-U34 | 192.168.10.75 | Online | Yes | Yes | N/A | Yes | NO | PDU [Raritan] PX4-5256CR-C8E8A0 | Yes | Outlet 8 | Yes | Medium
Kepler | BMW Old-Rack | Dell Inc. | PowerEdge R750 | CNFCP0032L00VK | U35-U36 | 192.168.10.123 | Online | Yes | Yes | Yes | Yes | Yes | PDU [Raritan] PX4-5256CR-C8E8A0 | Yes | Outlet 6 | Yes | High
Inoue | BMW Old-Rack | Dell Inc. | PowerEdge R740 | CNIVC0022P2057 | U37-U38 | 192.168.10.124 | Online | Yes | Yes | Yes | Yes | Not checked | PDU [Raritan] PX4-5256CR-C8E8A0 | Yes | Outlet 10 | Yes | High
5.12.9.11.4.8.6.10

## Server資源總表
Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue | Server
機櫃/Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | 機櫃/Rack
PDU Power Available | Dashboard shows PDU source, trend missing | No | No | Dashboard shows PDU source, trend unknown | No | Yes | No | Dashboard shows PDU source, trend missing | No | Dashboard shows PDU source, trend missing | Dashboard shows PDU source, trend missing | Dashboard shows PDU source, trend missing | Dashboard shows PDU source, trend missing | PDU Power Available
CPU Count | 1 | 1 | 2 | 2 |  | 2 | No | 1 | Unknown | Unknown | 2 | 2 | 2 | CPU Count
CPU Model | AMD EPYC 9354 32-Core Processor | Intel(R) Xeon(R) Gold 6433N | Intel(R) Xeon(R) Gold 6226R CPU @ 2.90GHz *2 | Intel(R) Xeon(R) Gold 6326 CPU @ 2.90GHz*2 | No | Intel(R) Xeon(R) CPU E5-2695 v4 @ 2.10GHz*2 | Unknown | Intel(R) Xeon(R) Gold 6433N | Unknown | Unknown | Intel Xeon processor*2 | Intel(R) Xeon(R) Gold 6326 CPU @ 2.90GHz*2 | Intel(R) Xeon(R) Gold 6226R CPU @ 2.90GHz | CPU Model
CPU Temp Available | Yes | Yes | Yes | Yes | No | Yes | Unknown | Yes | Unknown | Unknown | Yes | Yes | Yes | CPU Temp Available
Memory Available | Yes | Yes | Yes | Yes | No | Yes | Unknown | Yes | Unknown | Unknown | Yes | Yes | Yes | Memory Available
Storage Available | Yes | N/A | Yes | Yes | No | No | Unknown | N/a | Unknown | Unknown | Partial | Yes | Yes | Storage Available
Network Available | Yes | Yes | Partial | Partial | No | Yes | Unknown | N/a | Unknown | Unknown | Yes | Partial | Partial | Network Available
Redfish Power Available | Yes | Yes | Yes | Yes | No | Yes | Unknown | Yes | Unknown | Unknown | N/a | Yes | Yes | Redfish Power Available
PSU Available | Yes | Yes | Yes | Yes | No | Yes | Unknown | Yes | Unknown | Unknown | N/a | Yes | Yes | PSU Available
Fan RPM Available | Yes(1~8) | Yes(1~5) | Yes(1~6) | Yes(1~6) | No | Yes | Unknown | Yes(1~3) | Unknown | Unknown | N/a | Yes(1-6) | Yes | Fan RPM Available
Inlet Temp Available | Yes | No | Yes(Inlet Ambient/Front Ambient)limit:42/70 | Yes(System Board Inlet Temp) | No | No | Unknown | N/a | Unknown | Unknown | N/a | Yes(System Board Inlet temp) | Yes(System Board Inlet temp) | Inlet Temp Available
Outlet Temp Available | No | No | No | Yes(System Board Exhaust Temp) | No | No | Unknown | No | Unknown | Unknown | N/a | Yes(System Board exhaust temp) | Yes(System Board exhaust temp) | Outlet Temp Available

## server sensor
System Board
Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue
1 | Inlet Temp(limit:45) | PCH Temp(limit:90) | P1 DIMM 1-6 (limit:90) | System Board Inlet Temp(limit:42) |  |  |  | PCH Temp(limit:90) |  |  | N/a | limited:42 | limited:47
2 | System Tepm(limit:85) | System Tepm(limit:85) | P1 DIMM 7-12 (limit:90) | System Board Exhaust Temp(limit:80) |  |  |  | System Temp(limit:85) |  |  | N/a | System Board Inlet Temp | System Board Inlet Temp
3 | Peripheral Temp(limit:85) | Peripheral Temp(limit:85) | P2 DIMM 1-6(limit:90) |  |  |  |  | Peripheral Temp(limit:85) |  |  | N/a | System Board Exhaust Temp | System Board Exhaust Temp
4 | SOC_VRM Temp(limit:100) |  | P2 DIMM 7-12(limit:90) | [7 empty] | N/a
5 | VDDIO_VRM Temp(limit:100) |  | HD Max(limit:60) | [7 empty] | N/a
6 | P1V1_VRM Temp(limit:100) |  | Stor Batt 1(limit:60) | [7 empty] | N/a
7 |  |  | VR P1(limit:115)
8 |  |  | VR P1 Mem 1(limit:115)
9 |  |  | VR P1 Mem 2(limit:115)
10 |  |  | VR P2 Mem 1(limit:115)
11 |  |  | VR P2 Mem 2(limit:115)
12 |  |  | Chipset(limit:100)
13 |  |  | BMC(limit:110)
14 |  |  | BMC Zone(limit:90)
15 |  |  | HD Controller(limit: 100)
16 |  |  | HD Cntlr Zone(limit:85)
17 |  |  | LOM Card Zone(limit:75)
18 |  |  | PCI 1(limit:100)
19 |  |  | PCI 1 Zone(limit:75)
20 |  |  | PCI 2 Zone(limit:75) | [7 empty] | N/a
21 |  |  | PCI 3 Zone(limit:75)
22 |  |  | Battery Zone(limit:75)
23
Memory
Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue
limit temp | limit:85 | limit:86 |  |  |  | limit:85 |  | limit:85 |  |  | N/a
1 | DIMMA~F Temp | DIMMA~D Temp |  |  |  | P1-DIMMA1 Temp |  | DIMMA~D Temp(limit:85) |  |  | N/a
2 | DIMMG~L Temp | DIMME~H Temp |  |  |  | P1-DIMMB1 Temp |  | DIMME~H Temp(limit:85) |  |  | N/a
3 | [5 empty] | P1-DIMMC1 Temp |  |  |  |  | N/a
4 | [5 empty] | P1-DIMMD1 Temp |  |  |  |  | N/a
5 | [5 empty] | P2-DIMME1 Temp |  |  |  |  | N/a
6 | [5 empty] | P2-DIMMF2 Temp |  |  |  |  | N/a
7 | [5 empty] | P2-DIMMG1 Temp |  |  |  |  | N/a
8 | [5 empty] | P2-DIMMH1 Temp |  |  |  |  | N/a
9
10
StoageDevice
Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue
1 | AOC_SAS1 Temp(limit:105) | [9 empty] | N/a
2 | AOC_SAS2 Temp(limit:105) | [9 empty] | N/a
3 | HDD Temp Yes(limit:55) | [9 empty] | N/a
N/a
ASIC
Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue
1 | AIOM_NIC1 Temp(limit:100) | AIOM_NIC1 Temp(limit:100) | [5 empty] | AOC_NIC3 Temp(limit:100) |  |  | N/a
2
3
CPU
Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue
1 | CPU Temp(limit:100) | CPU_VRMIN Temp(limit:96) |  | limit: 100 |  | CPU1 Temp(limit:98) |  | CPU Temp(limit:96) |  |  |  | CPU1 Temp | CPU1 Temp
2 | CPU_VRM0 Temp (limit:100) | CPU_VRMON Temp(limit:100) |  | CPU1 Temp |  | CPU2 Temp(limit:98) |  | CPU_VRMIN Temp(limit:100) |  |  |  | CPU2 Temp | CPU2 Temp
3 | CPU_VRM1 Temp (limit:85) | CPU_VRMHV Temp(limit:100) |  | CPU2 Temp |  | PCH Temp(limit:95) |  | CPU_VRMON Temp(limit:100)
4 | [5 empty] | System Temp(limit:85) |  | CPU_VRMHV Temp(limit:100)
5 | [5 empty] | Peripheral Temp(limit:85)
6 | [5 empty] | MB_10G Temp(limit:100)
7 | [5 empty] | Vcpu1VRM Temp(limit:100)
8 | [5 empty] | Vcpu2VRM Temp(limit:100)
9 | [5 empty] | VmemABVRM Temp(limit:100)
10 | [5 empty] | VmemEFVRM Temp(limit:100)

## 延伸問題
| Q問題 | A答案 | 用途 | 原因 | 延伸問題 | 解決方式
1 | 要用哪些伺服器才可以穩定供應? | Quine/Davinci/Inoue/Kepler | 當主要CPU Temp 、Inlet temp、redfish power Dataset | 因為都有CPU Temp、Inlet Temp、Fan RPM Server Power、PDU Mapping、Online，所以可以長時間收集 | 1. 每個sever的sensor名稱、數量不同 | 1.需要標準化，才能輸入到模型。(例如:Front Ambient/System/Board Inlet Temp: Inlet_Temp)
[5 empty] | 2. 每個server廠牌、處理器、模型不同 | 2. 可以先同廠牌的server資料輸入至模型進行測試，再來測試不同廠牌/模型/處理器會有什麼影響

## Feature 定義
類別 | Feature | 原因
溫度 | CPU Temp | 主要預測目標，也可當歷史輸入
溫度 | Inlet temp | 代表進入伺服器的環境溫度
功率 | redfish power | 代表伺服器負載造成的熱源
散熱 | Fan RPM | 代表散熱強度

## Field_Guide
Section | Field / Data Item | Meaning | Example | How to Fill
Asset | Rack | Which rack contains the server | BMW Old-Rack | Read from asset detail page
Asset | U Position | Server physical location in rack | U37-U38 | Read from asset detail page
Collection | Redfish Data Available | Whether Redfish detail pages show telemetry | Yes / No / Unknown | Check Redfish information and data log tabs
Collection | PDU Outlet | Specific outlet connected to server | Outlet 10 | Read PDU socket block
Power | Redfish Power | Server power reported by BMC/Redfish | 243 W | Read power information / Redfish info tab
Power | PDU active_power | Outlet power measured by PDU | Outlet 10 active_power | Check InfluxDB or PDU dashboard
Thermal | CPU Temp | CPU temperature from Redfish | CPU1 70°C, CPU2 63°C | Read thermal sensor tab
Thermal | Inlet Temp | Server inlet temperature | 19°C | Read thermal tab
Cooling | Fan RPM | Fan speed reported by BMC | 5640 RPM | Read fan sensor tab
Workload | CPU Utilization | Host CPU usage from Node Exporter | 0% / Missing | Check performance metrics tab
Health | Health Status | Hardware health from Redfish | OK / Critical | Read overview tab